## Sheet1
Pressure at Treatment Station (psi) |  |  |  | 85
Pressure at Treatment Station (ft) |  |  |  | 36.7965
Pipe Diameter (in) |  |  |  | 12
Hazen-Williams Roughness Factor (ductile Iron) |  |  |  | 140
|  |  |  | Pre PRV |  |  | After PRV
Town | Pre PRV Usage (gpm) | Post PRV Usage (gpm) | Distance between Towns (mi) | Friction Loss in this segment of pipe (ft) | Pressure at this Town (ft) | Pressure at this Town (psi) | Friction Loss in this segment of pipe (ft) | Pressure at this Town (ft) | Pressure at this Town (psi)
A | 100 | 90 | 3 | 6.402 | 30.3945 | 70.2113 | 5.4044 | 31.3921 | 72.5158
B | 50 | 45 | 4 | 5.0132 | 25.3813 | 58.6307 | 4.2679 | 27.1243 | 62.6571
C | 70 | 60 | 5 | 4.4724 | 20.9088 | 48.2994 | 3.8331 | 23.2912 | 53.8026
D | 65 | 60 | 6 | 2.9227 | 17.9861 | 41.5479 | 2.6295 | 20.6617 | 47.7285
E | 45 | 40 | 2 | 0.42531 | 17.5608 | 40.5654 | 0.39173 | 20.27 | 46.8236
F | 70 | 70 | 4 | 0.33953 | 17.2213 | 39.7811 | 0.33953 | 19.9304 | 46.0393
Pressure required at Treatment Station to maintain 40 psi at Town F: |  |  |  |  | 78.7418